## Hackgut
[17 empty] | Kesseltypen | Leistung
[17 empty] | firematic 20 BioControl | 25
[17 empty] | firematic 35 BioControl | 35
Boiler type: | BioFire 800 BioControl |  | chosse boiler | [13 empty] | firematic 45 BioControl | 45
[17 empty] | firematic 60 BioControl | 65
Nominal load: |  | 800 | kW | [13 empty] | firematic 80 BioControl | 80
[17 empty] | firematic 100 BioControl | 101
Biomass type: |  | Beech | choose biomass |  | wood chips G30/G50 W35 according to ÖNORM M7133 | [11 empty] | firematic 130 BioControl | 130
Bulk desnity: |  | 558 | kg/FM | [13 empty] | firematic 151 BioControl | 150
Heat value Hu *: |  | 18.4 | MJ/kg - | 5.1111 | kWh/kg | [11 empty] | BioMatic 220 BioControl | 220
Ash softening point: |  | 1426 | °C | [13 empty] | BioMatic 250 BioControl | 250
Ash content * : |  | 0.5 | % | [13 empty] | BioMatic 300 BioControl | 300
*water free | [16 empty] | BioMatic 350 BioControl | 350
[17 empty] | BioMatic 400 BioControl | 400
Boiler Output in [kW] | Boiler Output in [%] | Water content in [%] | Moisture content in [%] | Heat value Hu in [kWh/kg] | Density of energy in [kWh/Srm] | Fuel consumption in [kg/h] | Efficieny ηf in [%] | Ash content in [kg/h] | [8 empty] | BioMatic 500 BioControl | 450
800 | 100 | 20 | 25 | 3.9635 | 1105.8289 | 219.3908 | 92 | 1.097 | [8 empty] | BioFire 500 BioControl | 500
800 |  | 25 | 33.3333 | 3.6881 | 1097.587 | 237.738 | 91.24 | 1.1887 | wassergehalt | 10% |  | 0% | 93 |  |  |  | BioFire 600 BioControl | 600
683.0297 |  | 30 | 42.8571 | 3.384 | 1079.02 | 260.3293 | 90.81 | 1.3016 | feuchte | 11.11% |  | 5% | 92.5579 |  |  |  | BioFire 800 BioControl | 800
625.1236 |  | 35 | 53.8462 | 3.0971 | 1063.5073 | 285.8288 | 90.37 | 1.4291 | FICHTE |  |  | 10% | 92.1178 |  |  |  | BioFire 1000 BioControl | 1000
567.2175 |  | 40 | 66.6667 | 2.8102 | 1045.4093 | 316.5146 | 89.94 | 1.5826 |  |  |  | 15% | 91.6799
509.3115 |  | 45 | 81.8182 | 2.5233 | 1024.0206 | 355.8638 | 89.09 | 1.7793 | tm bei 1t roh | 900 |  | 20% | 91.244
720 | 90 | 20 | 25 | 3.9635 | 1105.8289 | 197.4517 | 92 | 0.98726 |  |  |  | 25% | 90.8102
720 |  | 25 | 33.3333 | 3.6881 | 1097.587 | 213.9642 | 91.24 | 1.0698 | wasser bei 1t | 100 |  | 30% | 90.3785
614.7267 |  | 30 | 42.8571 | 3.384 | 1079.02 | 234.2963 | 90.81 | 1.1715 | Hu der TM | 16.92 |  | 35% | 89.9488
562.6113 |  | 35 | 53.8462 | 3.0971 | 1063.5073 | 257.246 | 90.37 | 1.2862 | Hu von 1t roh | 16.8818 |  | 40% | 89.5212
510.4958 |  | 40 | 66.6667 | 2.8102 | 1045.4093 | 284.8631 | 89.94 | 1.4243 | HU von 1 t roh | 4.6931 |  | 45% | 89.0956
458.3803 |  | 45 | 81.8182 | 2.5233 | 1024.0206 | 320.2774 | 89.09 | 1.6014 |  |  |  | 45% | 89.0956
640 | 80 | 20 | 25 | 3.9635 | 1105.8289 | 175.5126 | 92 | 0.87756
640 |  | 25 | 33.3333 | 3.6881 | 1097.587 | 190.1904 | 91.24 | 0.95095
546.4238 |  | 30 | 42.8571 | 3.384 | 1079.02 | 208.2634 | 90.81 | 1.0413
450.089 |  | 35 | 53.8462 | 3.0971 | 1063.5073 | 228.6631 | 90.37 | 1.1433
453.774 |  | 40 | 66.6667 | 2.8102 | 1045.4093 | 253.2117 | 89.94 | 1.2661 | [8 empty] | Brennstoff
407.4492 |  | 45 | 81.8182 | 2.5233 | 1024.0206 | 284.6911 | 89.09 | 1.4235 | [9 empty] | Hu in [MJ/kg] | Ascheerweichungspunkt [°C] | Ascheanteil wf |  | kg/FM
560 | 70 | 20 | 25 | 3.9635 | 1105.8289 | 153.5736 | 92 | 0.76787
560 |  | 25 | 33.3333 | 3.6881 | 1097.587 | 166.4166 | 91.24 | 0.83208 | [8 empty] | Spruce | 18.8 | 1426 | 0.6 |  | 379
478.1208 |  | 30 | 42.8571 | 3.384 | 1079.02 | 182.2305 | 90.81 | 0.91115 | [8 empty] | Beech | 18.4 | 1426 | 0.5 |  | 558
437.5865 |  | 35 | 53.8462 | 3.0971 | 1063.5073 | 200.0802 | 90.37 | 1.0004 | [8 empty] | Poplar | 18.5 | 1335 | 1.8 |  | 430
397.0523 |  | 40 | 66.6667 | 2.8102 | 1045.4093 | 221.5602 | 89.94 | 1.1078 | [8 empty] | Wicker | 18.4 | 1283 | 2 |  | 560
356.518 |  | 45 | 81.8182 | 2.5233 | 1024.0206 | 249.1047 | 89.09 | 1.2455
480 | 60 | 20 | 25 | 3.9635 | 1105.8289 | 131.6345 | 92 | 0.65817
480 |  | 25 | 33.3333 | 3.6881 | 1097.587 | 142.6428 | 91.24 | 0.71321
409.8178 |  | 30 | 42.8571 | 3.384 | 1079.02 | 156.1976 | 90.81 | 0.78099
375.0742 |  | 35 | 53.8462 | 3.0971 | 1063.5073 | 171.4973 | 90.37 | 0.85749
340.3305 |  | 40 | 66.6667 | 2.8102 | 1045.4093 | 189.9087 | 89.94 | 0.94954
305.5869 |  | 45 | 81.8182 | 2.5233 | 1024.0206 | 213.5183 | 89.09 | 1.0676
400 | 50 | 20 | 25 | 3.9635 | 1105.8289 | 109.6954 | 92 | 0.54848
400 |  | 25 | 33.3333 | 3.6881 | 1097.587 | 118.869 | 91.24 | 0.59435
341.5149 |  | 30 | 42.8571 | 3.384 | 1079.02 | 130.1646 | 90.81 | 0.65082
312.5618 |  | 35 | 53.8462 | 3.0971 | 1063.5073 | 142.9144 | 90.37 | 0.71457
283.6088 |  | 40 | 66.6667 | 2.8102 | 1045.4093 | 158.2573 | 89.94 | 0.79129
254.6557 |  | 45 | 81.8182 | 2.5233 | 1024.0206 | 177.9319 | 89.09 | 0.88966
320 | 40 | 20 | 25 | 3.9635 | 1105.8289 | 87.7563 | 92 | 0.43878
320 |  | 25 | 33.3333 | 3.6881 | 1097.587 | 95.0952 | 91.24 | 0.47548
273.2119 |  | 30 | 42.8571 | 3.384 | 1079.02 | 104.1317 | 90.81 | 0.52066
250.0495 |  | 35 | 53.8462 | 3.0971 | 1063.5073 | 114.3315 | 90.37 | 0.57166
226.887 |  | 40 | 66.6667 | 2.8102 | 1045.4093 | 126.6058 | 89.94 | 0.63303
203.7246 |  | 45 | 81.8182 | 2.5233 | 1024.0206 | 142.3455 | 89.09 | 0.71173
240 | 30 | 20 | 25 | 3.9635 | 1105.8289 | 65.8172 | 92 | 0.32909
240 |  | 25 | 33.3333 | 3.6881 | 1097.587 | 71.3214 | 91.24 | 0.35661
204.9089 |  | 30 | 42.8571 | 3.384 | 1079.02 | 78.0988 | 90.81 | 0.39049 | [5 empty] | 56.7155
187.5371 |  | 35 | 53.8462 | 3.0971 | 1063.5073 | 85.7487 | 90.37 | 0.42874
170.1653 |  | 40 | 66.6667 | 2.8102 | 1045.4093 | 94.9544 | 89.94 | 0.47477
152.7934 |  | 45 | 81.8182 | 2.5233 | 1024.0206 | 106.7591 | 89.09 | 0.5338
Technical details are subject to change. | [5 empty] | © HERZ Energietechnik GmbH 2011
The above calculations are based on the mentioned standards and relevant experience with HERZ biomass plants. The calculated values ​​may be more or less different and are related to biomass quality, bark content etc. | [7 empty] | ANKA
[10 empty] | Feuchte u (%) | Wassergehalt w (% der wasserhaltigen Masse) | bei 1 t TM (kg Wasser) | Summe TM+Wasser (kg) | TM bei 1 t roh (kg) | Wasser bei 1 t roh (kg) | Hu der TM (GJ) | Hu von 1 t roh (GJ/t roh) | Hu von 1 t roh (MWh/t roh) | kg/Rm | kg/Fm | kg/Sm³ | Hu MWh/Sm³
[9 empty] | Fichte | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 331.2937 | 473.75 | 189.5 | 0.76855
[9 empty] | Fichte | 33 | 25 | 330 | 1330 | 751.8797 | 248.1203 | 14.1353 | 13.5755 | 3.774 | 352.4965 | 504.07 | 201.628 | 0.76094
[9 empty] | Fichte | 43 | 30 | 430 | 1430 | 699.3007 | 300.6993 | 13.1469 | 12.4684 | 3.4662 | 378 | 540.54 | 216.216 | 0.74945
[9 empty] | Fichte | 54 | 35 | 540 | 1540 | 649.3506 | 350.6494 | 12.2078 | 11.4167 | 3.1738 | 407.0769 | 582.12 | 232.848 | 0.73902
[9 empty] | Fichte | 67 | 40 | 670 | 1670 | 598.8024 | 401.1976 | 11.2575 | 10.3523 | 2.8779 | 441.4406 | 631.26 | 252.504 | 0.72669
[9 empty] | Fichte | 82 | 45 | 820 | 1820 | 549.4505 | 450.5495 | 10.3297 | 9.3131 | 2.5891 | 481.0909 | 687.96 | 275.184 | 0.71247
[9 empty] | Buche | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 485.1399 | 693.75 | 277.5 | 1.1254
[9 empty] | Buche | 30 | 20 | 300 | 1300 | 769.2308 | 230.7692 | 14.4615 | 13.9409 | 3.8756 | 504.5455 | 721.5 | 288.6 | 1.1185
[9 empty] | Buche | 35 | 20 | 350 | 1350 | 740.7407 | 259.2593 | 13.9259 | 13.341 | 3.7088 | 523.951 | 749.25 | 299.7 | 1.1115
[9 empty] | Buche | 40 | 20 | 400 | 1400 | 714.2857 | 285.7143 | 13.4286 | 12.7839 | 3.5539 | 543.3566 | 777 | 310.8 | 1.1046
[9 empty] | Buche | 45 | 20 | 450 | 1450 | 689.6552 | 310.3448 | 12.9655 | 12.2653 | 3.4098 | 562.7622 | 804.75 | 321.9 | 1.0976
[9 empty] | Pappel | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 375.8741 | 537.5 | 215 | 0.87197
[9 empty] | Pappel | 30 | 20 | 300 | 1300 | 769.2308 | 230.7692 | 14.4615 | 13.9409 | 3.8756 | 390.9091 | 559 | 223.6 | 0.86658
[9 empty] | Pappel | 35 | 20 | 350 | 1350 | 740.7407 | 259.2593 | 13.9259 | 13.341 | 3.7088 | 405.9441 | 580.5 | 232.2 | 0.86118
[9 empty] | Pappel | 40 | 20 | 400 | 1400 | 714.2857 | 285.7143 | 13.4286 | 12.7839 | 3.5539 | 420.979 | 602 | 240.8 | 0.85579
[9 empty] | Pappel | 45 | 20 | 450 | 1450 | 689.6552 | 310.3448 | 12.9655 | 12.2653 | 3.4098 | 436.014 | 623.5 | 249.4 | 0.85039
[9 empty] | Weiden | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 489.5105 | 700 | 280 | 1.1356
[9 empty] | Weiden | 30 | 20 | 300 | 1300 | 769.2308 | 230.7692 | 14.4615 | 13.9409 | 3.8756 | 509.0909 | 728 | 291.2 | 1.1286
[9 empty] | Weiden | 35 | 20 | 350 | 1350 | 740.7407 | 259.2593 | 13.9259 | 13.341 | 3.7088 | 528.6713 | 756 | 302.4 | 1.1215
[9 empty] | Weiden | 40 | 20 | 400 | 1400 | 714.2857 | 285.7143 | 13.4286 | 12.7839 | 3.5539 | 548.2517 | 784 | 313.6 | 1.1145
[9 empty] | Weiden | 45 | 20 | 450 | 1450 | 689.6552 | 310.3448 | 12.9655 | 12.2653 | 3.4098 | 567.8322 | 812 | 324.8 | 1.1075
[9 empty] | Eiche | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 489.5105 | 700 | 280 | 1.1356
[9 empty] | Eiche | 30 | 20 | 300 | 1300 | 769.2308 | 230.7692 | 14.4615 | 13.9409 | 3.8756 | 509.0909 | 728 | 291.2 | 1.1286
[9 empty] | Eiche | 35 | 20 | 350 | 1350 | 740.7407 | 259.2593 | 13.9259 | 13.341 | 3.7088 | 528.6713 | 756 | 302.4 | 1.1215
[9 empty] | Eiche | 40 | 20 | 400 | 1400 | 714.2857 | 285.7143 | 13.4286 | 12.7839 | 3.5539 | 548.2517 | 784 | 313.6 | 1.1145
[9 empty] | Eiche | 45 | 20 | 450 | 1450 | 689.6552 | 310.3448 | 12.9655 | 12.2653 | 3.4098 | 567.8322 | 812 | 324.8 | 1.1075
[9 empty] | Pellets | 10 | 9 | 100 | 1100 | 909.0909 | 90.9091 | 17.1 | 16.8949 | 4.6968 | 430.7692 | 616 | 246.4 | 1.1573

## Pellets
[17 empty] | Kesseltypen | Leistung
[17 empty] | pelletstar 10 BioControl | 16 | 92
[17 empty] | pelletstar 20 BioControl | 21 | 92
Boiler type: | BioFire 600 BioControl |  | chosse boiler | [13 empty] | pelletstar 30 BioControl | 30 | 92
[17 empty] | pelletstar 45 BioControl | 45 | 92
Nominal load: |  | 600 | kW | [13 empty] | pelletstar 60 BioControl | 60 | 92
[17 empty] | firematic 20 BioControl | 25 | 91
Biomass type**: | Pellets ÖNORM M7135 |  | choose biomass | Pellets | [12 empty] | firematic 35 BioControl | 35 | 91
Water content |  | 10 | % | [13 empty] | firematic 45 BioControl | 45 | 91
Heat value Hu: |  | 18 | MJ/kg - | 5 | kWh/kg | [11 empty] | firematic 60 BioControl | 65 | 91
Density: |  | 1120 | kg/m³ | [13 empty] | firematic 80 BioControl | 80 | 91
Ash content: |  | 0.5 | % | [13 empty] | firematic 100 BioControl | 101 | 91
** for pelletstar and suction system only Pellets with Ø6mm diameter acceptable | [16 empty] | firematic 130 BioControl | 130 | 91
[17 empty] | firematic 151 BioControl | 150 | 91
Boiler Output in [kW] | Boiler Output in [%] | Water content in [%] | Moisture content in [%] | Heat value Hu in [kWh/kg] | Density of energy in [kWh/Srm] | Fuel consumption in [kg/h] | Efficieny ηf in [%] | Ash content in [kg/h] | [8 empty] | BioMatic 220 BioControl | 220 | ≥90
600 | 100 | 10 | 11.1111 | 5 | 1120 | 130.4348 | 92 | 0.65217 | [8 empty] | BioMatic 250 BioControl | 250 | ≥90
540 | 90 | 10 | 11.1111 | 5 | 1120 | 117.3913 | 92 | 0.58696 |  |  | wassergehalt | 10% |  | 0% | 93 |  | BioMatic 300 BioControl | 300 | ≥90
480 | 80 | 10 | 11.1111 | 5 | 1120 | 104.3478 | 92 | 0.52174 |  |  | feuchte | 11.11% |  | 5% | 92.5579 |  | BioMatic 350 BioControl | 350 | ≥90
420 | 70 | 10 | 11.1111 | 5 | 1120 | 91.3043 | 92 | 0.45652 |  |  | FICHTE |  |  | 10% | 92.1178 |  | BioMatic 400 BioControl | 400 | ≥90
360 | 60 | 10 | 11.1111 | 5 | 1120 | 78.2609 | 92 | 0.3913 | [5 empty] | 15% | 91.6799 |  | BioMatic 500 BioControl | 450 | ≥90
300 | 50 | 10 | 11.1111 | 5 | 1120 | 65.2174 | 92 | 0.32609 |  |  | tm bei 1t roh | 900 |  | 20% | 91.244 |  | BioFire 500 BioControl | 500 | ≥90
240 | 40 | 10 | 11.1111 | 5 | 1120 | 52.1739 | 92 | 0.26087 | [5 empty] | 25% | 90.8102 |  | BioFire 600 BioControl | 600 | ≥90
180 | 30 | 10 | 11.1111 | 5 | 1120 | 39.1304 | 92 | 0.19565 |  |  | wasser bei 1t | 100 |  | 30% | 90.3785 |  | BioFire 800 BioControl | 800 | ≥90
[11 empty] | Hu der TM | 16.92 |  | 35% | 89.9488 |  | BioFire 1000 BioControl | 1000 | ≥90
Technical details are subject to change. | [5 empty] | © HERZ Energietechnik GmbH 2011
The above calculations are based on the mentioned standards and relevant experience with HERZ biomass plants. The calculated values ​​may be more or less different and are related to biomass quality, bark content etc. | [7 empty] | ANKA
[14 empty] | 45% | 89.0956
Design your pellet storage room!
Live Storage | ~ | 70% flexible auger system | [14 empty] | Brennstoff
| ~ | 85% Transversal spring agitator | [15 empty] | Hu in [MJ/kg] | kg/m³ | Wassergehalt % | Ascheanteil wf |  | kg/FM
| ~ | 90% Horizontal spring agitator
[17 empty] | Pellets ÖNORM M7135 | 18 | 1120 | 10 | 0.5
Thumb rule -> pro 1kW heat load = 0,9m³ storage room (incl. dead zones) | [16 empty] | Pellets EN Plus A1 | 16.5 | 1000 | 10 | 0.7
[17 empty] | Pellets EN Plus A2 | 16.5 | 1000 | 10 | 1
Heat Load |  |  | 25 | kw | Write in yellow fields values​​! | [11 empty] | Pellets DIN Plus | 18 | 1120 | 10 | 0.5
Required storage size |  |  | 22.5 | m³
Gross storage volume (available) |  |  | 30 | m³
discharge system | Horizontal spring agitator
Nutzbarer Rauminhalt |  |  | 0.9
Storage area net |  |  | 27 | m³
Amount of pellets |  |  | 17550 | kg
[18 empty] | Flexible auger system | 0.7
Energy in storage |  |  | 87750 | kWh/kg | [13 empty] | Transversal spring agitator | 0.85
[18 empty] | Horizontal spring agitator | 0.9
Amount of energy equivalent to approximately: | 8775 | [l] Heating Oil |  | Hu= 10 kWh/kg
| 9236.8421 | [m³] Natural Gas |  | Hu= 9,5 kWh/kg
| 6855.4688 | [m³] LPG |  | Hu= 12,8 kWh/kg
| 12535.7143 | Kohle [kg] |  | Hu= 7 kWh/kg
Technical details are subject to change. | [5 empty] | © HERZ Energietechnik GmbH 2011
The above calculations are based on the mentioned standards and relevant experience with HERZ biomass plants. The calculated values ​​may be more or less different and are related to biomass quality, bark content etc. | [7 empty] | ANKA
56.7155
[10 empty] | Feuchte u (%) | Wassergehalt w (% der wasserhaltigen Masse) | bei 1 t TM (kg Wasser) | Summe TM+Wasser (kg) | TM bei 1 t roh (kg) | Wasser bei 1 t roh (kg) | Hu der TM (GJ) | Hu von 1 t roh (GJ/t roh) | Hu von 1 t roh (MWh/t roh) | kg/Rm |  | kg/Fm | kg/Sm³ | Hu MWh/Sm³
[9 empty] | Fichte | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 331.2937 |  | 473.75 | 189.5 | 0.76855
[9 empty] | Fichte | 33 | 25 | 330 | 1330 | 751.8797 | 248.1203 | 14.1353 | 13.5755 | 3.774 | 352.4965 |  | 504.07 | 201.628 | 0.76094
[9 empty] | Fichte | 43 | 30 | 430 | 1430 | 699.3007 | 300.6993 | 13.1469 | 12.4684 | 3.4662 | 378 |  | 540.54 | 216.216 | 0.74945
[9 empty] | Fichte | 54 | 35 | 540 | 1540 | 649.3506 | 350.6494 | 12.2078 | 11.4167 | 3.1738 | 407.0769 |  | 582.12 | 232.848 | 0.73902
[9 empty] | Fichte | 67 | 40 | 670 | 1670 | 598.8024 | 401.1976 | 11.2575 | 10.3523 | 2.8779 | 441.4406 |  | 631.26 | 252.504 | 0.72669
[9 empty] | Fichte | 82 | 45 | 820 | 1820 | 549.4505 | 450.5495 | 10.3297 | 9.3131 | 2.5891 | 481.0909 |  | 687.96 | 275.184 | 0.71247
[9 empty] | Buche | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 485.1399 |  | 693.75 | 277.5 | 1.1254
[9 empty] | Buche | 30 | 20 | 300 | 1300 | 769.2308 | 230.7692 | 14.4615 | 13.9409 | 3.8756 | 504.5455 |  | 721.5 | 288.6 | 1.1185
[9 empty] | Buche | 35 | 20 | 350 | 1350 | 740.7407 | 259.2593 | 13.9259 | 13.341 | 3.7088 | 523.951 |  | 749.25 | 299.7 | 1.1115
[9 empty] | Buche | 40 | 20 | 400 | 1400 | 714.2857 | 285.7143 | 13.4286 | 12.7839 | 3.5539 | 543.3566 |  | 777 | 310.8 | 1.1046
[9 empty] | Buche | 45 | 20 | 450 | 1450 | 689.6552 | 310.3448 | 12.9655 | 12.2653 | 3.4098 | 562.7622 |  | 804.75 | 321.9 | 1.0976
[9 empty] | Pappel | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 375.8741 |  | 537.5 | 215 | 0.87197
[9 empty] | Pappel | 30 | 20 | 300 | 1300 | 769.2308 | 230.7692 | 14.4615 | 13.9409 | 3.8756 | 390.9091 |  | 559 | 223.6 | 0.86658
[9 empty] | Pappel | 35 | 20 | 350 | 1350 | 740.7407 | 259.2593 | 13.9259 | 13.341 | 3.7088 | 405.9441 |  | 580.5 | 232.2 | 0.86118
[9 empty] | Pappel | 40 | 20 | 400 | 1400 | 714.2857 | 285.7143 | 13.4286 | 12.7839 | 3.5539 | 420.979 |  | 602 | 240.8 | 0.85579
[9 empty] | Pappel | 45 | 20 | 450 | 1450 | 689.6552 | 310.3448 | 12.9655 | 12.2653 | 3.4098 | 436.014 |  | 623.5 | 249.4 | 0.85039
[9 empty] | Weiden | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 489.5105 |  | 700 | 280 | 1.1356
[9 empty] | Weiden | 30 | 20 | 300 | 1300 | 769.2308 | 230.7692 | 14.4615 | 13.9409 | 3.8756 | 509.0909 |  | 728 | 291.2 | 1.1286
[9 empty] | Weiden | 35 | 20 | 350 | 1350 | 740.7407 | 259.2593 | 13.9259 | 13.341 | 3.7088 | 528.6713 |  | 756 | 302.4 | 1.1215
[9 empty] | Weiden | 40 | 20 | 400 | 1400 | 714.2857 | 285.7143 | 13.4286 | 12.7839 | 3.5539 | 548.2517 |  | 784 | 313.6 | 1.1145
[9 empty] | Weiden | 45 | 20 | 450 | 1450 | 689.6552 | 310.3448 | 12.9655 | 12.2653 | 3.4098 | 567.8322 |  | 812 | 324.8 | 1.1075
[9 empty] | Eiche | 25 | 20 | 250 | 1250 | 800 | 200 | 15.04 | 14.5888 | 4.0557 | 489.5105 |  | 700 | 280 | 1.1356
[9 empty] | Eiche | 30 | 20 | 300 | 1300 | 769.2308 | 230.7692 | 14.4615 | 13.9409 | 3.8756 | 509.0909 |  | 728 | 291.2 | 1.1286
[9 empty] | Eiche | 35 | 20 | 350 | 1350 | 740.7407 | 259.2593 | 13.9259 | 13.341 | 3.7088 | 528.6713 |  | 756 | 302.4 | 1.1215
[9 empty] | Eiche | 40 | 20 | 400 | 1400 | 714.2857 | 285.7143 | 13.4286 | 12.7839 | 3.5539 | 548.2517 |  | 784 | 313.6 | 1.1145
[9 empty] | Eiche | 45 | 20 | 450 | 1450 | 689.6552 | 310.3448 | 12.9655 | 12.2653 | 3.4098 | 567.8322 |  | 812 | 324.8 | 1.1075
[9 empty] | Pellets | 10 | 9 | 100 | 1100 | 909.0909 | 90.9091 | 17.1 | 16.8949 | 4.6968 | 430.7692 |  | 616 | 246.4 | 1.1573
Note on A1: Your User Name: